## System Cost
Cost estimate for a 'Renewable electric NEM'
All costs are real 2009-10 A$ | [9 empty] | hours/yr
Capacity, capacity factor and generation | [9 empty] | 8760
| Units | Hydro | PHES | PV | Wind | CST | OCGT | Total
Nameplate generation capacity | GW | 4.9 | 2.2 | 14.6 | 23.2 | 15.6 | 24 | 84.5 |  |  | http://www.ies.unsw.edu.au/docs/Solar2011-100percent.pdf
Capacity factor |  | 21% | 20% | 16% | 30% | 60% | 13.36% |  |  |  | http://www.ies.unsw.edu.au/docs/Solar2011-100percent.pdf
Annual generation | GWh | 9014.04 | 3854.4 | 20463.36 | 60969.6 | 81993.6 | 28098.576 | 204393.576 | 204400
Share |  | 4.41% | 1.886% | 10.01% | 29.83% | 40.12% | 13.75% | 100%
Capital Cost
| Units | Hydro | PHES | PV | Wind | CST | OCGT | Total
Capital cost rate | $/kW |  |  | 4650 | 2744 | 13362.7778 | 5050.5051 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Capital Cost | $bn |  |  | 67.89 | 63.6608 | 208.4593 | 121.2121 | 461.2223
Capital cost for transmission & distribution additions | $bn | [6 empty] | 106.7782
Total capital cost | $bn | [6 empty] | 568.0005
Levelised Cost of Electricity (LCOE)
| Units | Hydro | PHES | PV | Wind | CST | OCGT | Total
Technology LCOE | $/MWh | 50 | 300 | 394.1125 | 129.9956 | 285.8356 | 564.2894
System LCOE | $/MWh | 2.2051 | 5.6573 | 39.4575 | 38.7771 | 114.6645 | 77.5745 | 278.336
Add LCOE for the transmission & distribution additions | $/MWh | [6 empty] | 58.8878
Total LCOE | $/MWh | [6 empty] | 337.2238
CO2 Abatement Cost ($/t CO2)
System LCOE | $/MWh | [6 empty] | 337.2238
NEM 'LCOE' equiv. | $/MWh | [6 empty] | 45.4 |  | DRET (2011), Energy in Australia 2011, p22 | http://www.ret.gov.au/energy/Documents/facts-stats-pubs/Energy-in-Australia-2011.pdf
LCOE difference | $/MWh | [6 empty] | 291.8238
CO2 emissions factor for NEM | t/MWh | [6 empty] | 1 |  |  | http://www.climatechange.gov.au/~/media/publications/greenhouse-acctg/national-greenhouse-factors-july-2010-pdf.pdf
CO2 emissions factor per technology | t/MWh | [5 empty] | 0 |  |  |  | http://www.ret.gov.au/energy/Documents/AEGTC%202010.pdf
CO2 emissions factor for the system | t/MWh | [5 empty] | 0 | 0
CO2 emissions factor difference | t/MWh | [6 empty] | 1
CO2 abatement cost | $/t CO2 | [6 empty] | 291.8238
LCOE Inputs
| Units | Hydro | PHES | PV | Wind | CST | OCGT
Total Plant Cost (gross) | $/kW |  |  | 4650 | 2744 | 12026.5 | 5000 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Total Plant Cost (sent out) | $/kW |  |  | 4650 | 2744 | 13362.7778 | 5050.5051 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Plant Size (MW) | MW |  |  | 1x5, 10x5 | 500 | 200-300 | 0 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Capacity Factor | % |  |  | 16% | 30% | 60% | 13.37% |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Auxiliary Load | % |  |  | 0% | 0% | 10% | 1% |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Thermal Efficiency (HHV) | % |  |  | NA | NA | NA | 33% |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Fuel Cost | $/GJ |  |  | NA | NA | NA | 10 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
CO2 Transport and Storage |  |  |  | NA | NA | NA | 0 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Fixed O&M | $/kW-yr |  |  | 55 | 37 | 73 | 9 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Variable O&M | $/MWh |  |  | 0 | 0 | 0 | 2.5 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Plant Life | yr |  |  | 30 | 25 | 30 | 40 |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Discount rate | % |  |  | 10.1% | 10.1% | 10.1% | 10.1% |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Capital recovery factor |  |  |  | 0.10697 | 0.11102 | 0.10697 | 0.1032 |  |  |  | http://www.nrel.gov/analysis/tech_lcoe_documentation.html
LCOE Calculator
Capital Charges | $/MWh |  |  | 354.8716 | 115.9165 | 271.9467 | 445.0142
Fixed O&M Cost | $/MWh |  |  | 39.2409 | 14.0791 | 13.8889 | 7.6843
Variable O&M Cost | $/MWh |  |  | 0 | 0 | 0 | 2.5
CO2 Transport and Storage | $/MWh
Fuel Cost | $/MWh | [5 empty] | 109.0909
LCOE (Real 2009-10 A$) | $/MWh |  |  | 394.1125 | 129.9956 | 285.8356 | 564.2894
Calculate capital cost of CST with 15 h storage
CST Parabolic Trough w/out Storage | $/kW |  |  |  |  | 5109 |  |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
CST Parabolic Trough w 6 h Storage | $/kW |  |  |  |  | 7875.5 |  |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Cost of 6 h storage (i.e. the difference) | $/kW |  |  |  |  | 2766.5
Gross up to 15 h storage (i.e. x 15/6) | $/kW |  |  |  |  | 6916.25
Add the cost of CST with no storage | $/kW |  |  |  |  | 12025.25
Cost multiplier (ie for 15 h compared with 6 h storage) | [5 empty] | 1.5269
Auxilliary load | [5 empty] | 10% |  |  |  |  | http://www.ret.gov.au/energy/facts/Pages/EnergyFacts.aspx
Capital cost (sent out) | $/kW |  |  |  |  | 13361.3889
Note on A5: Peter Lang: Capacities are from EDM-2011.
Note on A6: Peter Lang: Capacity factors, except hydro and PHES, are from EDM-2011. EDM-2011. did not state the generation from hydro and PHES, but states it was calculated by the model to provide the amount of generation required. The hydro and PHES numbers here are from subtraction of the other generation from the total generation (204.4 TWh).
Note on A7: Peter Lang: Generation is calculated from capacity x capacity factor.
Note on A8: Peter Lang: Each technology's contribution to the total energy generated.
Note on A12: Peter Lang: Capital cost unit rates are for 'sent out'. These are converted from the DRET figures. 'Sent Out = Gross / (1 - Auxiliaries Load) '.
Note on A13: Peter Lang: 'Capacity' x 'Capital cost rate'. (GW * $/GW)
Note on A26: Peter Lang: assume the equivalent to the LCOE of the existing NEM plants = average wholesale price of electricity. NEM average wholesale price in 2009-10 was $45/MWh
Note on A29: Peter Lang: Emissions factor is for combustion only. Emissions factor for renewables = 0 t CO2/MWh Emissions factor for fossil fuels is from: EPRI(2010) http://www.ret.gov.au/energy/Documents/AEGTC%202010.pdf and from ACIL Tasman (2010) http://www.aemo.com.au/planning/0400-0019.pdf.
Note on A30: Peter Lang: Emissions factor for each technology x the proportion of the total electricity generated by that technology.
Note on A49: Peter Lang: For explanation of Capital Recovery Factor (CRF) refer to: http://www.nrel.gov/analysis/tech_lcoe_documentation.html
Note on C7: Peter Lang: Actual hydro generation in 2010 (approximately). 2009-10 = 12,522 GWh, 2008-09 = 11,052 GWh, 2007-08 = 12,057 GWh.
Note on C12: Peter Lang: no capital cost for the existing hydro capacity
Note on D12: Peter Lang: no capital cost for Wivenhoe PHES.
Note on D19: Peter Lang: PL's guess. Would buy renewable energy when it would otherwise be spilled and would have to sell at about 4 times the buy cost. If we assume it is bought at average $75/MWh, then LCOE is 4 x $75/MWh = $300/MWh.
Note on E12: Peter Lang: This is the average of the DRET high and low estimate for 5 MW fixed plate solar PV. I suspect this is far too low for average, residential, roof-top, PV, which averages about 2 kW per installation. I'd suggest the LCOE for PV by a factor of 1.5 to 2. This has not been done in these calculations.
Note on E19: Peter Lang: DRET cost is for 5MW units of fixed plate PV. However, residential PV will be a factor of about 1000 smaller, so the costs will be much higher (for installation, maintenance, decomissioning, etc). The performance, across the whole system, will deteriorate faster with residential PV than with a commercially maintained solar farm. So the true LCOE would be higher than calculated from the DRET inputs I've used the DRET high cost, but suspect it should be about 1.5 to 2 times this. Calculated - see LCOE inputs and LCOE calculator below.
Note on F12: Peter Lang: This is the average of the DRET high and low estimate for 'Wind Turbine, Large Scale'. I suspect this is too low given that ABARE's summaries of Major Electricity Projects gives the average cost for new wind farms (in 2009 which is the year for all the costs in the EPRI, ACIL Tasman, Worley Parsons and DRET reports) as about $2,900/kW.
Note on F19: Peter Lang: DRET Wind, Large Scale, 500 MW plant size, average of low and high cost. Calculated, see LCOE Inputs and LCOE Calculator below.
Note on G12: Peter Lang: This is the most significant component of the capital cost and the LCOE of the EDM-2011 system. After the biofuelled gas turbines, CST is the figure that is least well substantiated. The DRET figures for CST are for 6 hours of storage. However,EDM-2011 assumed 15 hours of storage. That would mean the solar field multiplier and the energy storage capacity would be 2.5 times larger than the 6 hour system on which the DRET capital cost estimate is based. I've estimated the CST with 15 hours storage would be 1.53 x the DRET capital cost. See the inputs and calculations at the bottom of this spreadsheet.
Note on G19: Peter Lang: Calculated, see LCOE Inputs and LCOE Calculator below
Note on H12: Peter Lang: Crude estimate for biofuel system. See Lang (2012) for explanation.
Note on H19: Peter Lang: Calculated, see LCOE Inputs and LCOE Calculator below
Note on H29: Peter Lang: Emissions factor: = 0 t/CO2/MWh for gas turbines running on biofuels, and = 0.622 t/MWh for OCGT running on natural gas (at optimum efficency; emissions would be higher in practice - see Lang (2012) paper for more explanation.
Note on H30: Peter Lang: Emissions factor for each technology x the proportion of the total electricity generated by that technology.
Note on I14: Peter Lang: From tab 'Trans cost'
Note on I21: Peter Lang: From tab 'Trans cost'
Note on I26: Peter Lang: 2009-10 Weighted average wholesale price of electricity in the NEM = $45.40 DRET (2011), p22, http://www.ret.gov.au/energy/Documents/facts-stats-pubs/Energy-in-Australia-2011.pdf.
Note on I28: Peter Lang: Weighted average of the NEM states' emissions factor (Table 5, DCCEE (2010), NGA Factors, http://www.climatechange.gov.au/~/media/publications/greenhouse-acctg/national-greenhouse-factors-july-2010-pdf.pdf Weighted average using generation per state in 2009-10 from: http://bree.gov.au/documents/data/energy/ausenergystats/[TableO200910.xls
Note on J7: Peter Lang: NEM demand 2010 quoted by EDM-2011. This is the target generation. The total generation must equal this target. Increase this target to include extra generaton needed to compensate for line losses. This cell is not used in any calculations. It is purely a convenient place to put the target you are aiming to meet with your selection of capacity and capacity factors for the technologies.

## Trans cost
Cost estimates for transmission system additions
"Copper-plate" transmission additions
From | to | Capacity (GW) | Length (km) | MW.km | Unit Cost ($/MW.km) | Capital Cost |  |  |  | Source URL
Woomera | Adelaide | 2.6 | 518 | 1346800 | 1500 | 2020200000
Nullarbor | Adelaide | 2.6 | 1196 | 3109600 | 1500 | 4664400000
White Cliffs | Hay | 2.6 | 485 | 1261000 | 1500 | 1891500000
Roma | Brisbane | 2.6 | 477 | 1240200 | 1500 | 1860300000
Longreach | Brisbane | 2.6 | 1177 | 3060200 | 1500 | 4590300000
Tibooburra | Mildura | 2.6 | 630 | 1638000 | 1500 | 2457000000
Wind |  | 23.2 | 300 | 6960000 | 1500 | 10440000000
Adelaide | Melbourne | 9.6754 | 729 | 7053366.6 | 1500 | 10580049900
Adelaide | Sydney | 16.1191 | 1408 | 22695750.3237 | 1500 | 34043625485.5629
Hobart | Melbourne | 2.3321 | 800 | 1865662.9771 | 3000 | 5596988931.3846
Melbourne | Sydney | 5.9264 | 909 | 5387102.9577 | 1500 | 8080654436.4905
Sydney | Brisbane | 7.3128 | 1000 | 7312830 | 1500 | 10969245000
Brisbane | Cairns | 0.3 | 1707 | 512100 | 1500 | 768150000
Total |  |  | 11336 |  |  | 97962413753.4381
LCOE of 'Copper-plate' additions
Capital cost |  |  |  |  | $ | 97962413753.4381 | 8815800000
Capacity (NEM peak demand) |  |  |  |  | MW | 33758 | 33758 |  | Table 1.1 | http://www.accc.gov.au/content/item.phtml?itemId=961581&nodeId=8d9cbc63c61c99def2e544adb08cad6d&fn=Chapter%201%20National%20Electricity%20Market.pdf
Capital cost unit rate |  |  |  |  | $/kW | 2901.9022 | 261.147
Book life |  |  |  |  | years | 40 | 40
Energy transmitted |  |  |  |  | MWh | 198256000 | 198256000 |  | Table 2.1 | http://www.accc.gov.au/content/item.phtml?itemId=1021485&nodeId=840e2a3729b8cb0221cb851494ff9f9c&fn=Chapter%202%20Electricity%20networks.pdf
Load factor | [5 empty] | 67.04% | 67.04%
LCOE (capital component only) |  |  |  |  | $/MWh | 50.9927 | 4.5889
LCOE (O&M component) |  |  |  |  | $/MWh | 0.68333 | 2.6229
LCOE, Transmission additions |  |  |  |  | $/MWh | 51.676 | 7.2118
Capital cost and LCOE of 'Copper-plate' additions to transmission and distribution system
Capital cost - Transmission & distribution |  |  |  |  | $ bn | 106.7782
LCOE Transmission & distribution |  |  |  |  | $/MWh | 58.8878
LCOE Inputs (Real 2009-10 A$)
[5 empty] | Units | Transmission | Distribution
Asset Life |  |  |  |  | yr | 40 | 40
Discount rate |  |  |  |  | % | 10.1% | 10.1%
Capital recovery factor | [5 empty] | 0.1032 | 0.1032 |  |  | http://www.nrel.gov/analysis/tech_lcoe_documentation.html
Capital cost unit rate |  |  |  |  | $/kW | 2901.9022 | 261.147
Load Factor |  |  |  |  | % | 67.04% | 67.04%
Fixed O&M |  |  |  |  | $/kW-yr | 4.0131 | 15.4038
Variable O&M |  |  |  |  | $/MWh | 0 | 0
LCOE Calculator
Capital Charges |  |  |  |  | $/MWh | 50.9927 | 4.5889
Fixed O&M |  |  |  |  | $/MWh | 0.68333 | 2.6229
Variable O&M |  |  |  |  | $/MWh | 0 | 0
LCOE (Real 2009-10 A$) |  |  |  |  | $/MWh | 51.676 | 7.2118
O&M costs - Transmission & Distribution
http://www.hes.edu.au/resources/2979/HES-29520%20AUPN%20-%20Article%20-%20Energy%20market%202010%20report.pdf
| p56 | In the current five year cycle, transmission
businesses will each spend, on average, around
$100 million per year on operating and maintenance
costs. In distribution, operating costs per business are
forecast at around $200 million per year.
[6 empty] | Transmission | Distribution | Trans | Dist
No. of businesses | [5 empty] | 5 | 13 | p56 | p56 | http://www.hes.edu.au/resources/2979/HES-29520%20AUPN%20-%20Article%20-%20Energy%20market%202010%20report.pdf
O&M per business per year |  |  |  |  | $ million | 100 | 200 | p56 | p56 | http://www.hes.edu.au/resources/2979/HES-29520%20AUPN%20-%20Article%20-%20Energy%20market%202010%20report.pdf
O&M |  |  |  |  | $ million | 500 | 2600
Generaton, 2010 |  |  |  |  | MWh | 204400000 | 204400000
Cost of electricity |  |  |  |  | $/MWh | 2.4462 | 12.7202
Transmission and Distribution Capex and Opex for NEM 2010
From: AER (2011) State of the Energy Market 2011, Chapter 2, "Electricity Networks"
http://www.accc.gov.au/content/item.phtml?itemId=1021485&nodeId=840e2a3729b8cb0221cb851494ff9f9c&fn=Chapter%202%20Electricity%20networks.pdf
[6 empty] | Transmission | Distribution | Trans | Dist
Capex |  |  |  |  | $ billion | 1.6 | 6.5 | Fig 2.5 | Fig 2.5 | http://www.accc.gov.au/content/item.phtml?itemId=1021485&nodeId=840e2a3729b8cb0221cb851494ff9f9c&fn=Chapter%202%20Electricity%20networks.pdf
Opex |  |  |  |  | $ billion | 0.5 | 2.3 | from above | pers comm
electricity transmitted |  |  |  |  | GWh | 198256 | 198256 | Table 2.1 | Table 2.1 | http://www.accc.gov.au/content/item.phtml?itemId=1021485&nodeId=840e2a3729b8cb0221cb851494ff9f9c&fn=Chapter%202%20Electricity%20networks.pdf
Capex |  |  |  |  | $/MWh | 8.0704 | 32.7859
Opex |  |  |  |  | $/MWh | 2.522 | 11.6012
total |  |  |  |  | $/MWh | 10.5924 | 44.3871
Asset value |  |  |  |  | $ billion | 13.09 | 44.079 | Table 2.1 | Table 2.2 | http://www.accc.gov.au/content/item.phtml?itemId=1021485&nodeId=840e2a3729b8cb0221cb851494ff9f9c&fn=Chapter%202%20Electricity%20networks.pdf
line length |  |  |  |  | km | 41838 | 747213 | Table 2.1 | Table 2.2 | http://www.accc.gov.au/content/item.phtml?itemId=1021485&nodeId=840e2a3729b8cb0221cb851494ff9f9c&fn=Chapter%202%20Electricity%20networks.pdf
Cost "Copper-plate" additions proportion of NEM 2010 | [5 empty] | 27.09% | 20%
O&M for transmission & distribution additions
NEM line length |  |  |  |  | km | 41838
Copperplate additions |  |  |  |  | km | 11336
O&M for transmission & distribution additions |  |  |  |  | $/MWh | 0.68333 | 2.3202
Note on A40: Peter Lang: For explanation of Capital Recovery Factor (CRF) refer to: http://www.nrel.gov/analysis/tech_lcoe_documentation.html
Note on C4: Peter Lang: Generating capacity for each technology specified in EDM-2011. Capacity of the interstate interconnector lines estimates as described in Lang (2012)
Note on D4: Peter Lang: distances from Google Maps
Note on D11: Peter Lang: Average distance to a capital city or an entry point to a trunk line.
Note on F4: Peter Lang: $/MW.km derived from the SA Interconnector study (2011). http://www.electranet.com.au/assets/Uploads/interconnectorfeasibilitystudyfinalnetworkmodellingreport.pdf The unit cost is a rough average for 2000 MW normal capacity AC and HVDC lines. So this cost rate assumes a mix of AC and HVDC lines.
Note on F14: Peter Lang: Cost rate doubled to account for the under sea component. Say 2/3 on land at $1,500/MW.km and 1/3 under sea cable at $6,000/MW.km
Note on G22: Peter Lang: Table 1.1: http://www.accc.gov.au/content/item.phtml?itemId=961581&nodeId=8d9cbc63c61c99def2e544adb08cad6d&fn=Chapter%201%20National%20Electricity%20Market.pdf
Note on G25: Peter Lang: Electricity transmistted by NEM in 2010; see Table 2.1, http://www.accc.gov.au/content/item.phtml?itemId=1021485&nodeId=840e2a3729b8cb0221cb851494ff9f9c&fn=Chapter%202%20Electricity%20networks.pdf
Note on G27: Peter Lang: from LCOE calculator below
Note on G28: Peter Lang: from LCOE calculator below
Note on G43: Peter Lang: Total Opex for NEM in 2010 divided by peak power transmitted (i.e. peak demand) multiplied by 'Copper-plate' line length proportion of total NEM line length.
Note on G81: Peter Lang: Proportion is based on line length ('Copper-plate' / NEM)
Note on G86: Peter Lang: NEM Opex for 2010 x 'Copper-plate' proportion of NEM
Note on H21: Peter Lang: 20% of the value of the NEM's distribution assets in 2010. (from below)
Note on H41: Peter Lang: Capital cost of distribution upgrades divided by peak demand
Note on H43: Peter Lang: Total Opex for NEM in 2010 divided by peak power transmitted (i.e. peak demand) multiplied by 'Copper-plate' proportion of NEM Opex for Distribution in 2010.
Note on H81: Peter Lang: Assumption (see Lang 2012)
Note on H86: Peter Lang: NEM Opex for 2010 x 'Copper-plate' proportion of NEM

## NEM CO2 intensity
NEM CO2 Intensity, 2009-10
http://www.climatechange.gov.au/~/media/publications/greenhouse-acctg/national-greenhouse-factors-july-2010-pdf.pdf
| 2009-10 | CO2-e EI
| GWh | t CO2-e/MWh | t CO2-e
NSW | 74393.7 | 0.9 | 66954.33
VIC | 54629.9 | 1.23 | 67194.777
Qld | 61710 | 0.89 | 54921.9
SA | 13949.9 | 0.72 | 10043.928
TAS | 10404.1 | 0.32 | 3329.312
NEM | 204683.5 | 0.98906 | 202444.247
|  | Table 5: | http://www.climatechange.gov.au/~/media/publications/greenhouse-acctg/national-greenhouse-factors-july-2010-pdf.pdf
| Table O: | http://bree.gov.au/data/energy/AES-2011.html
Note on C10: Peter Lang: Calculated